## Tabelle1
Parameterliste
D01 | Start setp. | 5.5 bar
D02 | End Defrosting Temp | 13.0 grad
D03 | Defrosting Cycle | 45 min.
D04 | Max. Duration | 8 min.
D06 | Defrost type | NOR.
D07 | Out Temp when Defrost | 2.0 Grad
D08 | Compensation offset | 2.0 bar
D09 | Defrost out Temp. Deviation | 14.0 Grad
D10 | Defrost ending pressure | 2.8 bar
E01 | EEV mode | Auto.
E02 | Super heat | 6.0 Grad
E03 | Init place | 250 N
E04 | Min. place | 100 N
E05 | Defrost place | 480 N
E06 | Cooling place | 480 N
E07 | EEV exhaust set temp. | 60.0 Grad
E09 | EEV step propartion value | 2
E10 | EEV step integral value | 10
E11 | EEV step differential value | 0
E12 | Super heatcompen. Differ | 0.0 Grad
F01 | Speed | DC 1 (Inverter)
F02 | Cooling high speed pressure | 15.0 bar
F03 | Cooling low speed pressure | 7.0 bar
F04 | Cooling motor off pressure | 2.0 bar
F05 | Heating high speed pressure | 3.0 bar
F06 | Heating low speed presure | 9.0 bar
F07 | Heating motor off pressure | 11.0 bar
F11 | Fan Motor Heat Max. Speed | 800r
F12 | Cooling Fan Motor Speed | 700 r
F13 | Fan Motor Min. Speed in Heating | 600 r
F14 | Timer Mute Start | 13 h
F15 | Timer Mute End | 12 h
F16 | Mute Mode Speed | 500 r
F17 | Timer Mute ON/OFF | OFF
F18 | Manual Fan motor Speed | OFF
F19 | DC/EC Fan Rated Speed | 600 r
F20 | PWM Detect/antifreeze Temp. | Temp.
H01 | Power down memory | YES
H02 | Mode type | Heat pump
H06 | Heating Min. frequency | 20 Hz
H07 | Cooling Min. frequency | 40 Hz
H08 | Heating Max. frequency | 30 Hz
H09 | Cooling Max. frequency | 80 Hz
H10 | Delay off time | 120 min.
H11 | Auto mode restarting time | 192 min.
H12 | Compessor type | 2
H13 | Comp. Defrost Frequency | 80 Hz
H14 | Frequency Cycle of 0.2 Grad | 20 min.
H15 | Comp. Overcurren Protect | 20.0 A
H16 | Refrigerant type | R410a
H17 | Cool start Compenlow temp. | 15.0 Grad
H18 | Cool stop Compenlow temp. | 5.0 Grad
H19 | Cool Max. frequency low temp. | 70 Hz
H20 | Cool start Compenhigh temp. | 35.0 Grad
H21 | Cool stop Compenhigh temp. | 43.0 Grad
H22 | Cool stop Frequency high temp. | 70 Hz
H23 | Heat start Compen.low temp. | 15.0 Grad
H24 | Heat stop Compen. low temp. | -10.0 Grad
H25 | Heat Max. frequency low temp. | 90 Hz
H26 | Heat start Compen. high temp. | 35.0 Grad
H27 | Heat stop Compen. high temp. | 43.0 Grad
H28 | Heat Max. frequence high temp | 80 Hz
H29 | Max. pressure sensor valve | 20.0 bar
H30 | Min. pressure sensor valve | 0.0 bar
H31 | Ambient temp. before commpen. | 2.0 Grad
H31 | Ambient temp. after commpen. | 15.0 Grad
H33 | Max. Frequence silent comp. | 25 Hz
H34 | Comp. Stop | -15.0 Grad
H35 | Temp Difference of Start Freq. | 10.0 Grad
H36 | Start Frequency | 30 Hz
H37 | Unit Adress | 0
P01 | Mode | Interval
P02 | Intervale | 30 min
P03 | Duration | 3 min
P04 | Advance | 1 min
R09 | Max. cool | 35.0 Grad
R10 | Min. heat | 6.0 Grad
R11 | Max. heat | 43.0 Grad
U02 | 1l. Water Pulse | 0 Hz
H03 | Temperatur unit | Grad
| modbus slave address | 1